## Registers
|  | Macromatic PC1MDUL |  |  | Modbus Register Map |  |  | PMD7Z04 June 2021
Category | Sub-category | Description | Register | Units | Word Size | Data Type | Access | Comments | Default
Device Configuration |  |  | 0 - 999
| Manufacturing | Model | 0 | -- | 4 | STRING | R |  | "PC1MDUL"
|  | Manufacturer | 50 | -- | 18 | STRING | R |  | "MACROMATIC INDUSTRIAL CONTROLS, INC."
| Device Software | Firmware Revision | 105 | -- | 3 | UINT16 | R
| Communications | IP Address | 108 | -- | 4 | UINT16 | R |  | 192.168.0.5
|  | Subnet Mask | 112 | -- | 4 | UINT16 | R |  | 255.255.255.0
|  | Default Gateway | 116 | -- | 4 | UINT16 | R |  | 192.168.0.100
|  | MODBUS Unit ID | 120 | -- | 1 | UINT16 | R |  | 255
|  | IP Address User Settings | 121 | -- | 4 | UINT16 | RW |  | 192.168.0.5
|  | Subnet Mask User Settings | 125 | -- | 4 | UINT16 | RW |  | 255.255.255.0
|  | Default Gateway User Settings | 129 | -- | 4 | UINT16 | RW |  | 192.168.0.100
| Physical Address | MAC Address | 150 | -- | 6 | UINT16 | R | (All products datecode 2127 and later)
Timekeeping |  |  | 1000 - 1999
| System Date/Time | Year | 1000 | -- | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Month | 1001 | -- | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 0-12 (All products datecode 2127 and later) | 0
|  | Day | 1002 | -- | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 1-31 (All products datecode 2127 and later) | 0
|  | Hour | 1003 | Hours | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 0-23 (All products datecode 2127 and later) | 0
|  | Minutes | 1004 | Minutes | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 0-59 (All products datecode 2127 and later) | 0
|  | Seconds | 1005 | Seconds | 1 | UINT16 | RW | (Read-Only when SNTP is enabled via coil 1000) Range: 0-59 (All products datecode 2127 and later) | 0
|  | Time Since Last Update | 1007 | Seconds | 1 | UINT16 | R | (Read-Only when SNTP is enabled via coil 1000) Range: 0-65535 (All products datecode 2127 and later) | 0
| SNTP Configuration | SNTP Server | 1100 | -- | 13 | STRING | RW | (Requires enabling SNTP via coil 1000) IPv4 address or URL of the SNTP server. (All products datecode 2127 and later) | "3.pool.ntp.org"
|  | SNTP Time Zone Adjust | 1200 | H | 1 | INT16 | RW | (Requires enabling SNTP via coil 1000) Range: ±23. (All products datecode 2127 and later) | 0
Measurement Data |  |  | 2000 - 19999
| Voltage | Phase L1 - L2 Voltage | 3000 | V | 2 | FLOAT32 | R | Voltages below 30V will display as zero.
|  | Phase L2 - L3 Voltage | 3002 | V | 2 | FLOAT32 | R | Voltages below 30V will display as zero.
|  | Phase L3 - L1 Voltage | 3004 | V | 2 | FLOAT32 | R | Voltages below 30V will display as zero.
|  | Average L - L Voltage | 3006 | V | 2 | FLOAT32 | R | Voltages below 30V will display as zero.
|  | Phase L1 - N Voltage | 3008 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) Voltages below 30V will display as zero.
|  | Phase L2 - N Voltage | 3010 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) Voltages below 30V will display as zero.
|  | Phase L3 - N Voltage | 3012 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) Voltages below 30V will display as zero.
|  | Average L - N Voltage | 3014 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) Voltages below 30V will display as zero.
|  | Voltage Unbalance | 3022 | % | 2 | FLOAT32 | R
| Frequency | Average Frequency | 5000 | Hz | 2 | FLOAT32 | R
| Temperature | Internal Device Temperature | 11000 | degree C | 1 | INT16 | R
Monitor Settings |  |  | 20000 - 29999
| Voltage | Nominal L - L Voltage Setting | 22000 | V | 2 | FLOAT32 | R | 190 , 208 , 220 , 240 , 380 , 480 , 600
|  | Nominal L - N Voltage Setting | 22002 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) 110 , 120 , 127 , 139 , 220 , 277 , 346
|  | Voltage Band | 22014 | % | 2 | FLOAT32 | R | 5-20% of Nominal Voltage (All products datecode 2127 and later)
|  | L - L Average Overvoltage Trip Threshold | 22016 | V | 2 | FLOAT32 | R | 5 - 20% of Nominal Voltage Setting
|  | L - L Average Undervoltage Trip Threshold | 22018 | V | 2 | FLOAT32 | R | -5 - 20% of Nominal Voltage Setting
|  | Phase L - N Average Overvoltage Trip Threshold | 22032 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) 5 - 20% of Nominal Voltage Setting
|  | Phase L - N Average Undervoltage Trip Threshold | 22034 | V | 2 | FLOAT32 | R | (Requires enabling 3P4W via coil 1761) -5 - 20% of Nominal Voltage Setting
|  | Phase Unbalance Trip Threshold | 22036 | % | 2 | FLOAT32 | R | 2 - 10% of Average Voltage
Faults |  |  | 30000 - 39999
| Fault Delays | Reset Delay | 30000 | seconds | 2 | FLOAT32 | R | 1.0 - 300.0 seconds Applies to product startup and trip reset
|  | Reset Delay Remaining | 30002 | seconds | 2 | FLOAT32 | R | remaining reset delay
|  | Fault Trip Delay | 30004 | seconds | 2 | FLOAT32 | R | 0.3 - 30.0 seconds
|  | Fault Trip Delay Remaining | 30006 | seconds | 2 | FLOAT32 | R | remaining fault trip delay
| Fault Records | Fault Record 1: Fault Type | 31000 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 1: Year | 31001 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 1: Month | 31002 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 1: Day | 31003 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 1: Hour | 31004 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 1: Minutes | 31005 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 1: Seconds | 31006 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Fault Type | 31010 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 2: Year | 31011 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Month | 31012 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Day | 31013 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Hour | 31014 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Minutes | 31015 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 2: Seconds | 31016 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Fault Type | 31020 | -- | 1 | UINT16 | R | See "Fault Types" sheet for definition of faults | 0
|  | Fault Record 3: Year | 31021 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Month | 31022 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Day | 31023 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Hour | 31024 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Minutes | 31025 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 3: Seconds | 31026 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Fault Type | 31030 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 4: Year | 31031 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Month | 31032 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Day | 31033 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Hour | 31034 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Minutes | 31035 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 4: Seconds | 31036 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Fault Type | 31040 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 5: Year | 31041 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Month | 31042 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Day | 31043 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Hour | 31044 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Minutes | 31045 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 5: Seconds | 31046 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Fault Type | 31050 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 6: Year | 31051 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Month | 31052 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Day | 31053 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Hour | 31054 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Minutes | 31055 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 6: Seconds | 31056 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Fault Type | 31060 | -- | 1 | UINT16 | R | See "Fault Types" sheet for definition of faults | 0
|  | Fault Record 7: Year | 31061 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Month | 31062 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Day | 31063 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Hour | 31064 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Minutes | 31065 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 7: Seconds | 31066 | seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Fault Type | 31070 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 8: Year | 31071 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Month | 31072 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Day | 31073 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Hour | 31074 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Minutes | 31075 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 8: Seconds | 31076 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Fault Type | 31080 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 9: Year | 31081 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Month | 31082 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Day | 31083 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Hour | 31084 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Minutes | 31085 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 9: Seconds | 31086 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Fault Type | 31090 | -- | 1 | UINT16 | R | 0: Normal 1: Phase Loss 2: Phase Reversal 3: Phase Unbalance 4: Overvoltage 5: Undervoltage | 0
|  | Fault Record 10: Year | 31091 | -- | 1 | UINT16 | R | Range: 0-65535 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Month | 31092 | -- | 1 | UINT16 | R | Range: 1-12 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Day | 31093 | -- | 1 | UINT16 | R | Range: 1-31 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Hour | 31094 | Hours | 1 | UINT16 | R | Range: 0-23 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Minutes | 31095 | Minutes | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0
|  | Fault Record 10: Seconds | 31096 | Seconds | 1 | UINT16 | R | Range: 0-59 (All products datecode 2127 and later) | 0

## Coils
Category | Sub-category | Description | Coil | Access | Comments | Default
Device Configuration
| Network Settings | Save IP Address Settings | 0 | RWc |  | 0
|  | Save Subnet Mask Settings | 1 | RWc |  | 0
|  | Save Default Gateway Settings | 2 | RWc |  | 0
|  | Enable Auto-Negotiation | 3 | RW |  | 1
|  | Link Speed | 4 | RW | 0 : 10Mbit/s 1 : 100Mbit/s Read-only if Auto-Negotiation is enabled | 1
|  | Link Duplex | 5 | RW | 0 : Half Duplex 1 : Full Duplex Read-only if Auto-Negotiation is enabled | 1
|  | DHCP | 6 | RW | 0 : Not Enabled 1 : Enabled | 0
| Timekeeping Configuration | Date/Time Update Method | 1000 | RW | 0 : Update Via Modbus 1 : Update Via SNTP (All products datecode 2127 and later) | 0
| Voltage Monitor Settings | Nominal Frequency | 1760 | RW | 0 : 50Hz 1 : 60Hz | 1
|  | 3-Phase Wiring | 1761 | RW | 0 : 3P-4W 1 : 3P-3W | 1
Faults
| Voltage Monitor Fault Status | No Fault | 3360 | R |  | 0
|  | Phase Loss | 3361 | R |  | 0
|  | Phase Reversal | 3362 | R |  | 0
|  | Phase Unbalance | 3363 | R |  | 0
|  | System Overvoltage | 3364 | R |  | 0
|  | System Undervoltage | 3365 | R |  | 0
|  | Relay Status | 4000 | R | 0 : Relay Not Energized 1 : Relay Energized (All products datecode 2127 and later)
|  | Manual Reset Enable | 4956 | R
| Fault Record Settings | Clear Fault History | 16000 | RWc | Clear all recorded faults | 0
|  | Record Limit Behavior | 16001 | RW | 0 : Do not add new fault records when limit hit 1 : Delete oldest fault record when limit hit | 1

## Data Types
Data Type | Definition
UTF8 | Unicode character
STRING | Null-terminated string, HiLo byte order
UINT16 | Unsigned 16-bit integer
INT16 | Signed 16-bit integer
UINT32 | Unsigned 32-bit integer
FLOAT32 | 32-bit floating point number, big-endian

## Access Types
Acces Type | Definition
R | Read
W | Write
Wc | Writing 1 to coil will set the coil. Coil will automatically clear to 0 after function is performed.